## Slide 1: To Recover or Sequester? - Holistic Approaches to Managing Phosphorus (and Struvite) through Anaerobic Digestion
TEXAS ASSOCIATION OF CLEAN WATER AGENCIES
MARCH 22, 2024

## Slide 2: Introductions
Director of Wastewater Innovation and Senior Process Specialist
With Hazen since 2012
Over 20 years of experience in all things water, including sidestream nutrient management and recovery projects (HRSD, Gwinnett County, Metro Water Recovery, etc.)
Principal investigator and technical advisor on 10+ WRF projects
Wendell Khunjar, PhD
Brandt Miller, PE
Texas Wastewater Practice Leader
WEAT Municipal Resource Recovery & Design and Nutrient Committee Member
Over 16 years of experience including BNR design, process modeling, and operations support
Technical lead on over $650M in WRF design projects across Texas

## Slide 3: What is the Fate of Phosphorus at WRRFs?
Liquid Effluent
Solids
Phosphorus
90+% of influent P can be present in the solids
Recycle

## Slide 4: Managing Solids and Sidestream Nutrients is a Challenge
Solids stabilization can release a large amount of P (and N, Mg, Ca, Fe, etc.)
Primary and/or secondary treatment
Thickening
Stabilization
Dewatering
Residuals management
Nuisance precipitate formation
Challenges with effluent compliance
Increased labor, chemicals, etc.
Notes: Slug loads in recycle

## Slide 5: Solids and Sidestream Nutrient Characteristics Drive Precipitate Formation Potential
Sidestream nitrogen content
Sidestream phosphorus content
EBPR +
THP + AnD
EBPR – enhanced biological phosphorus removal
THP – thermal hydrolysis
AnD – anaerobic digestion
AeD – aerobic digestion
PAD - Post aerobic digestion
HTNS – holding tank and no stabilization
**NO3
EBPR + HTNS
Chem P + HTNS
Biomass uptake + HTNS
EBPR + AnD/AeD**
EBPR +
PAD**
Chem P +
THP + AnD
Chem P + AD/AeD**
Chem P +
PAD**
Struvite
(Mg + NH3 + PO4)
Brushite
(Ca + PO4)
Vivianite
(Fe + PO4)
Precipitant
Type:
Notes: Precipitate potential
Chemical is left side, ortho-p low

## Slide 6: Several Strategies Exist for Navigating Challenges Associated with High Solids and Sidestream P
Dilution
Acid addition
Chemical addition
Nitrogen removal
Chemical precipitation
Sequestration
Recovery
MANAGE precipitate formation after it forms
Mechanical cleaning
SUPPRESS precipitate formation by manipulating chemistry
MINIMIZE precipitate formation by removing chemical constituent
INTENTIONAL precipitate formation and facilitate removal
These options do not reduce P or N recycle load
These options do reduce P and/or N recycle load
Notes: Let it form, suppress it, minimize potential, intentionally form where you want it/can control it

## Slide 7: Solids and Sidestream Phosphorous Sequestration and Recovery Options
Headworks
Primary Clarification
BNR
Secondary Clarification
Disinfection
Thickener
Anaerobic Digestion
Dewatering
Biosolids
Effluent
Influent
WAS
Septage
Thickener Filtrate
Dewatering Filtrate
Nutrient Recovery Option
Struvite
MagPrex
Nuresys*
EloVac
Sequestration vs. Harvesting configurations
SOLIDS STREAM (PRE-DEWATERING) OPTIONS
Nutrient Recovery Option
Struvite
WAS release
Ostara
Paques
Nuresys*
Struvia
CalPrex
LIQUID STREAM (POST-DEWATERING) OPTIONS
Chemical Precipitation

## Slide 8: Sequestration vs. Recovery
Form precipitate and retain in the sludge
Form precipitate and extract from centrate/filtrate
Nucleation
Crystal Growth
Aggregation
Form precipitate and extract from sludge
Nucleation
Crystal Growth
Aggregation
Nucleation
Crystal Growth
Aggregation
Dominated by small crystals
Mix of small and large particles
Sequestration
Recovery
(from sludge)
Recovery
(from centrate)
Notes: Nucleation – first step to form single crystal layer
Grow
Aggregate

## Slide 9
Sequestration
Recovery
(from sludge)
Sidestream P load
Scaling potential reduction
Recovery
(from centrate)
Biosolids dewatering
Biosolids nutrient content reduction
Recovered product potential
Implementation Costs
Notes: Scaling potential reduction

## Slide 10: To Sequester or Recover?
Metro Water Recovery Robert W. Hite Treatment Facility
Denver
Notes: Our first case study involves a pre-dewatering phosphorus recovery system at the Robert W Hite Treatment Facility owned and operated by the Metro Wastewater Reclamation District.
We’ve partnered with the District and Stantec to plan, design, and construct a phosphorus recovery system at this facility.

## Slide 11: Robert W. Hite Treatment Facility (RWHTF)
220 mgd WRRF
Influent TP ~ 5 mg/L
Future Effluent TP Limits
Notes: The Hite facility is a 220 mgd WRRF located in Denver
Influent TP averages 5 mg/L
Future effluent TP limits may be as stringent as 0.1 mg/L

## Slide 12: Combination of EBPR and AD Results in Significant Struvite Formation in Digester and Dewatering Complex
Cake
GVTs
Primary Sludge
GTE to NSEC SARs/SSEC
SHT 3
Dewatering
DAFT
Secondary Sludge
Underflow (DAFnate) to IPW
CST
DMX
Return to NSEC CARRBs
SHT 2
Overflow
(ConWAS)
Return to SSEC CARRBs
Digestion
Formation of up to 2,000+ lb P/day of nuisance precipitate
Sidestream represents
26% of Inf TP,
25% of Inf TKN

## Slide 13: Multiple Drivers for Phosphorus Management
5 Measures for Success
Break the phosphorus recycle loop
Struvite-scale issues for O&M
Biosolids dewatering costs
Phosphorus loading on soils
Recovery of a finite resource
1 lb of phosphorus equates to 8 lbs of struvite
7,000 lbs of phosphorus enter the RWHTF each day!

## Slide 14: Multiple Concepts Evaluated for RWHTF
Sequestration/Recovery
MagPrex
Thickener
Anaerobic Digestion
Dewatering
Nutrient Recovery Option
Biosolids
WAS
Thickener Filtrate
Dewatering Filtrate
WAS Release
Sequestration/ Recovery Option
PS
Recovery only
Ostara + WASSTRIP
CalPrex
Return to main plant

## Slide 15: Sequestration/Recovery
MagPrex
MagPrex
Courtesy CNP

## Slide 16: Recovery
WASSTRIP + Pearl
CalPrex
Release tank
Pre-dewatering
Primary solids
WAS
dWAS
Dewatering
Cake
CalPrex
Brushite

## Slide 17: Evaluation Results
MagPrex
CalPrex
Sidestream P load
Scaling potential
WASSTRIP + Ostara
Polymer reduction
Recovered product potential
Implementation Costs
$16.9M
$11.8M
$21.8M
300 lb/day
470 lb/day
650 lb/day
1,300 lb/day
1,900 lb/day
1,000 lb/day
14 to 18%
Cake %TS (increase)
Site-specific piloting needed
5 to 10%
3 to 5%
0 to 2%
410 lb/day
2,100 lb/day
1,900 lb/day

## Slide 18
MagPrex Process Flow Diagram for RWHTF
7 to 10 hour HRT
Notes: CNP’s MagPrex a relatively simple system that primarily requires Ortho-P and NH4 from digested sludge, magnesium addition, process aeration to raise the pH, and hydraulic residence time
In order to facilitate struvite formation:
  Anaerobically digested sludge is pumped to the MagPrex reactor
  Blowers are used for air stripping of carbon dioxide to increase the pH of the digested sludge since struvite forms more readily at higher pH
  Magnesium chloride is dosed into the reactor since it’s the limiting nutrient for struvite formation
Anti-foam can be dosed to the top of the reactor to mitigate foaming if needed
Struvite settles in the reactor cone so it can be periodically removed using the struvite pump
There are three primary operating modes that determine where struvite removed from the reactor goes:
  In Recovery Mode – Struvite flows to the struvite classifier where it’s washed and then discharged to a dumpster
  In Recycle Mode – Struvite is recycled to the top of the reactor so fine crystals can grow larger to enhance struvite recovery
  In Sequester Mode – Sequestered struvite is routed to a holding tank and onward to dewatering

## Slide 19: Lessons Learned Since Commissioning
Chart: Ortho-P Conversion (%)
80+% oP reduction
Chart: Polymer dose, lb/dt Cake solids, %
| Polymer Dose (lb/dt) | Cake Solids (%)
Untreated | 41.5122 | 21.3636
MagPrex Treated | 32.1913 | 21.1842
20+% polymer demand reduction ($575K/year savings)
Minimal benefits on cake %TS at present

## Slide 20: Lessons Learned Since Commissioning
Struvite capture lower than anticipated
Reactor cleaning is challenging
Nuisance precipitation decreased downstream reactors…
…struvite still present in feedlines to reactors
Alkalinity losses impact sidestream deammonification

## Slide 21: Design and Implementation Takeaways
Influent and Primary Sludge Screening important
Low-profile, vertically oriented diffusers are recommended
  Avoid Wide-band, horizontally oriented diffusers
Eliminate upper diffusers
  Metro turned off upper with no process impacts
Process control for aeration/alkalinity control if coupled with deammonification
Notes: Complex scaffolding was erected between the reactor’s inner and outer shells and throughout the inside of the reactor to facilitate welding and coating as well as diffuser installation.
Upstream screening is critical to protecting AirPrex and reliable operation. Fine screening of influent wastewater and additional screening of primary sludge is recommended to prevent rags/wipes from accumulating inside the reactor as shown in attached photos. We understand influent wastewater is screened by coarse screens and 6 mm perforated plate screens. In addition, a strain press is suggested for primary sludge screening.
It appears the Haifa design includes low-profile, vertically oriented diffusers. Low-profile, vertically oriented diffusers like the ones shown in the attached photos are recommended. Wide-band, horizontally oriented diffusers are not recommended. At Metro, rags/wipes have accumulated on wide-band diffusers and some have broken off as shown in the attached photos.
It appears the Haifa design includes lower diffusers, but not upper diffusers. That configuration is preferable and upper diffusers are not recommended. Metro’s upper diffusers have proven problematic and were recently turned off without any negative process impacts. Some of the upper diffusers sheared off due to the combination of upward forces from the lower diffusers and downward forces from rags/wipes.

## Slide 22: To Sequester or Recover?
Recovery most efficient from dewatering stream;
Lower recovery from sludge matrix
Need to balance oP conversion with pellet growth
Fines formation and capture important
Process can be simpler
Can operate with or without exogenous chemical addition
Multiple options for sequestration
EloVac, MagPrex, Nuresys
Key to understand P, N, Mg and Ca balances at facility
Both options break recycling load effectively
Sequestration
Recovery
?

## Slide 23: Questions?
wkhunjar@hazenandsawyer.com
703-267-2759
Wendell Khunjar, PhD PE
Brandt Miller, PE, PMP
bmiller@hazenandsawyer.com
469-250-3784

## Slide 24: To Recover or Sequester? - Holistic Approaches to Managing Phosphorus (and Struvite) through Anaerobic Digestion
TEXAS ASSOCIATION OF CLEAN WATER AGENCIES
MARCH 22, 2024