## Slide 1
Process Intensification Opportunities in MBRs
Latest Trends and Results
Jose Jimenez, PhD, PE, BCEE, WEF Fellow
March 22nd, 2024

## Slide 2: Agenda
Membrane Bioreactor | Energy Conservation | Densification + MBR | Peak Flow Management

## Slide 3: Conventional Activated Sludge Process
M
AEROBIC
RAS
PE
SE
AEROBIC
ANOXIC
WAS
IMLR
SWING

## Slide 4: Choosing MBR over ASP
Higher water quality generated
its smaller footprint
Key disadvantages are the operational complexity and the cost
  the capital (or investment) cost, CAPEX and
  the operational cost, OPEX.

## Slide 5: Membrane Bioreactor
Dupont (Memcor) membrane
Hollowfiber membrane
Flat-plate membrane

## Slide 6: MBR Advantages MBR Disadvantages
Fully automated
Compact footprint
High UVT values
Complete solids removal
Nutrient removal
Microconstituent, pathogens and bacterial removal
Simpler process
Requires fine screening of influent:
  <3.0 mm flat sheet
  <2.0 mm hollow fiber
High capital cost
High energy cost for air scour
Membrane maintenance and replacement
Dissolved oxygen management and BNR

## Slide 7: MBR Disadvantages
Requires fine screening of influent:
  <3.0 mm flat sheet
  <2.0 mm hollow fiber
High capital cost
High energy cost for air scour
Membrane maintenance and replacement
Dissolved oxygen management and BNR
Chart: 2 MLD O&M Costs
| Elec. Other | Process Air | Scour Air | Chem | Memb Repl | Labor
 | 67940.9884 | 216354.6415 | 328794.2422 | 32267.764 | 611348.2869 | 118800
Chart: 20 MLD O&M Costs
| Elec. Other | Process Air | Scour Air | Chem | Memb Repl | Labor
All | 626128.8475 | 2516568.7958 | 1871696.9512 | 309937.377 | 5371856.6407 | 839700

## Slide 8: Energy Requirements in MBR
Pellegrin and Kinnear (2012)
CAS – 1,500 – 3,000 kWh/MG

## Slide 9: Benefits of MBRs
Reduced footprint
As low as 40% of conventional
High quality effluent
Low turbidity, BOD, TSS
Pathogen removal
Better trace organics removal
Ease of Operations
Fewer unit processes
Eliminates sludge settleability issues
Highly automated
Constructability
Modular expansion capability
Excellent for retrofits
Tier 1 Pathogen Reduction Credits |  | 
 | WaterVal (Aus) | WRF 4997 (US)
Virus | 1.5 | 2.4
Bacteria | 4 | 4.5
Protozoa | 2 | 2.5

## Slide 10: MBR Process Operations
Air Scour
Highest energy usage of MBR operation
Trend toward lower air flow designs
“Sludged” Flat Sheet Cassette
“Sludged” Hollow Fiber Module
RAS Circulation
4 to 6 times forward flow
Bioreactor/MBR MLSS of 0.6-0.8
Maintain MLSS in MBR
  8-10 g/L long term
  12-14 g/L short term
Chemical Cleaning
Maintenance cleaning
Chemical enhanced backwash
Recovery clean

## Slide 11: MBR – MLSS and Aeration

## Slide 12: Process Considerations Pretreatment
Fine Screens
  Best is 2mm round opening
  No possibility of bypass
  100% redundancy at peak flow
Fat, Oil and Grease: typ. <150mg/L
Flux rates
  Function of ML suspended solids and temperature
  30-day average typically 10-15 GPD/ft2
  Up to 30 GPD/ft2 for 2-4 hours
Lighthouse Point WWTP, Blaine WA – 1.5 MGD

## Slide 13: Process Considerations Biological Process
High SRT (>10 days typical)
Fully nitrifying conditions
Bioreactor MLSS typically 6,000-10,000mg/L
High MLSS = reduced OTR, esp. in fine bubble aeration
Filaments and bulking common, but not a concern as with clarifiers
Foam management

## Slide 14: Aeration control technologies

## Slide 15: Aeration Control Technologies for Biological Process Energy Reduction
Aeration controls such as ABAC or AvN™ can maintain DO conc. of 0.1 to < 1.0 mg/L.
Some low-DO ASP achieve limits-of-technology effluent water quality
Low-DO ASP require less energy and organic carbon than conventional aeration system (e.g., DO > 1.0 mg/L)

## Slide 16: DO Cascade Control Loops
Airflow Setpoint Bands
Min required for mixing
Max to protect diffusers
DO Setpoint Bands
Min = 1.0 mg-O2/L
Max = 2.0 mg-O2/L

## Slide 17: Ammonia Based Aeration Control (ABAC) Feedback ABAC
NH4/NOx
DO
M
FIT
_
+
PID
NH4
Setpoint
_
+
PID
%
Opening
Airflow
Setpoint
_
+
PID
DO
Setpoint
Target BNR Effluent
Aerobic Zone = 1-2 mg-N/L
Airflow Setpoint Bands
Min required for mixing
Max to protect diffusers
DO Setpoint Bands
Min = 0.2 mg-O2/L
Max = 2.5 mg-O2/L

## Slide 18: Ammonia versus NOx (AvN) Control
Target BNR Effluent
Aerobic Zone NH4/NOx = target
Airflow Setpoint Bands
Min required for mixing
Max to protect diffusers
DO Setpoint Bands
Min = 0.2 mg-O2/L
Max = 2.5 mg-O2/L

## Slide 19: On-line Instrumentation for Nitrogen Removal

## Slide 20: Energy Reduction Using Aeration Controls

## Slide 21: MBR + Densified Activated Sludge

## Slide 22: MBR + densification = memDENSE
Performance of membranes with MBR are limited by the characteristics of the mixed liquor
memDENSE allows controlling and stabilizing sludge characteristics (biological matrix)
Fundamentals
wash out low value inventories
bio-accumulate high value inventories
biology
membrane
lower cake layer resistance, lower super fine colloidal organics < 1.5 microns in Membrane Tank
Notes: All disciplines that touch a water project (I&C, electrical, structural etc.)
Operator focused (CEO has operator licenses)
Owners Agent to Construction experience

## Slide 23: What does densification do? Separation of undesirable biomass
overflow
underflow
excess biological sludge
dense flocs > 200 µm
PAOs (dark)
Nitrifiers (AOB, NOB)
light & small flocs < 100 µm
filaments
filaments
PAO
pin & light flocs
large & dense flocs (AOB, NOB)
(feed)
(OF)
(UF)

## Slide 24: What does densification do? Improved and stabilized bio-process
Before
After memDENSE
Early steady-state

## Slide 25: What does densification do? Particle size distribution
80th percentile particle size increase from 160µm to 210µm
Overflow (WAS) Underflow
Startup Steady state

## Slide 26: What does densification do? Densified MBR – effect on permeability
Maintained high permeability with temperature drop
Less recovery cleans
10-15 gfd/psi increase over pre densification

## Slide 27: Peak flow management

## Slide 28: Process Analysis and Selection
Single Train (Example)
Dual Train (Example)
Brown and Caldwell
28
FEATURES
Single, unified treatment train
MBR used for all flow
ADVANTAGES
Single unified biology
Less equipment to operate and maintain
No blending of different effluent qualities
Allows reuse of infrastructure
Allows for gravity discharge without need for effluent pump station
DISADVANTAGES
Potential for higher capital cost
Depending on approach selected, may not optimize use of existing plant infrastructure
FEATURES
Split treatment trains
MBR used for some flow, existing treatment for other flow
ADVANTAGES
Makes greatest use of existing plant infrastructure
DISADVANTAGES
Two separate biologies to maintain
More difficult and complex operations and maintenance
VS

## Slide 29: Wet Weather Management Opportunities
Equalization
In-line EQ in new process tanks
Retrofit existing secondary clarifiers
Separate WW Treatment
Brown and Caldwell
29

## Slide 30: King County’s Brightwater WWTP Split Treatment
During Wet Weather Operations:
Primary clarifiers are converted to CEPT
Fe/polymer addition is activated
Portion of PE goes to MBR
Wet weather flow is bypassed and blended with MBR effluent before disinfection
Brown and Caldwell
30

## Slide 31: City of San Mateo, CA Nutrient Removal and Wet Weather Flow Management Upgrades
Use of Bio-Actiflo for treating wet weather flow was selected for the following reasons:
Proven technology and performance
When blended with MBR effluent, produces an effluent that meets current NPDES permit limits
Ease of operation
Quick startup
Small footprint
Brown and Caldwell
31

## Slide 32: Thank you.
Questions?
Jose Jimenez, PhD, P.E., BCEE
Wastewater Innovation Leader jjimenez@brwncald.com