## Slide 1: Reducing Risk at the District’s Riverbend WWTP Influent Lift Station
Paul Banschbach, PE

## Slide 2: Over the next 20 minutes, we will discuss the following..
Existing Lift Station Capacity & Condition Concerns
Alternatives Overview
Bidding Update

## Slide 3: Existing Lift Station Capacity & Condition Concerns

## Slide 4: The existing west influent lift station serves the area north of Lewisville Lake in the Riverbend WRP service area.
36” inverted siphon

## Slide 5: Fast moving developments required urgent capacity upgrades at the lift station.
2019
2025

## Slide 6: Based on system modeling and pending developments, the WILS needed to be upgraded from 6.2 MGD to 9 MGD with buildout flows exceeding 17 MGD.
Existing Flows1 (MGD) |  |  |  | Future Flows (MGD) |  |  | 
 | Fishtrap (R17) | Brewer (R4) | Total |  | Fishtrap2 (R17) | Brewer3 (R4) | Total
Average Daily Flow | 0.55 | 1.00 | 1.55 | Average Daily Flow | 1.26 | 0.99 | 2.25
Peak Average Daily Flow | 0.88 | 1.60 | 2.48 | Peak Average Daily Flow | 2.00 | 1.50 | 3.50
Average Daily Wet-Weather Flow | 1.38 | 2.50 | 3.88 | Average Daily Wet-Weather Flow | 3.16 | 2.48 | 5.64
Peak Wet-Weather Flow | 2.20 | 4.00 | 6.20 | Peak Wet Weather Flow | 5.04 | 3.96 | 9.00

## Slide 7: With the existing wet well depth and configuration, regular maintenance is challenging resulting in severe condition issues.
60’
Pump guiderails are corroded

## Slide 8: Velocities through the existing inverted siphon are below 2 FPS causing sediment deposition creating issues at the lift station during flushing events

## Slide 9: The USACE is the primary external stakeholder, and any new easement requests come with lengthy permitting efforts.
Brewer Blvd.
Fish Trap Road

## Slide 10: Alternatives Overview

## Slide 11: We initially investigated rehabilitating the existing lift station but identified multiple high-risk concerns
11

## Slide 12: The nearest manhole is on the north side of the lake limiting bypass pumping options for the lift station rehab.

## Slide 13: To bypass the wet well for rehabilitation, a second 60’+ suction pit would need to be installed on the south side of the Lake requiring high risk construction
Bypass pumping was estimated to be $2.5M+

## Slide 14: An 18-inch dry weather flow siphon could be installed to increase scouring velocities, but the existing siphon would still be utilized for peak events

## Slide 15: Additional easements from the USACE would be needed for installation of the dry weather siphon adding schedule risk

## Slide 16: The 60’ deep wet well would remain a challenge to maintain with limited operational flexibility
60’

## Slide 17: Replacing the pumps in the wet well would increase capacity; however, full build out flows would not be achieved resulting in a second future lift station.
Garver recommends replacing all pumps to 7.5 MGD for total pumping capacity of 15 MGD
Improvements identified in Lift Stations Condition Assessments Report (August 2022)
Recoat surfaces within wet well and associated site manholes
Replace 10-inch ductile iron discharge piping in the wet well
Perform electrical maintenance work on electrical and I/C assets, including level transducer and pump pressure gauges
Replace pump guide rails in the wet well
Replace VFD for Pump No. 3
Replace submersible pump

## Slide 18: The rehabilitation alternative could be implemented quickly but came with significant cons
Immediate capacity relief with bypass pumping operations
WILS can be upgraded to pump 15 MGD
ADF siphon barrel should improve sediment and rag issues
Quickest to implement
Lowest Cost
Cons
Pros
Additional gravity infrastructure in USACE property
Further expansion of WILS (>15 MGD) will be challenging
High-risk bypass operation
Two siphon barrels to maintain and operate
WILS wet well remains at 60’ deep
Significant cost spent on bypass and not on infrastructure

## Slide 19: We identified major risks associated with the upgrading the existing lift station
High risk bypass pumping
Limited ability to fix the sediment issues in the inverted siphon
The 60-foot-deep wet well is not maintainable
The full buildout flows would likely require a second lift station
Potential permitting delays with the USACE

## Slide 20: To mitigate the rehabilitation risks, we proposed relocating the lift station to the north side of the lake
New 10 MGD lift station
New 24-inch force main
Decommission WILS
Bypass pumping eliminated!

## Slide 21: The lake crossing was designed as a force main with increased velocities to limit sediment deposition
21

## Slide 22: To minimize USACE permitting, the lake crossing was proposed to be installed by HDD to limit deep pits in the floodplain and additional permitting needs.

## Slide 23: A new lift station wet well provided the opportunity to design for ease of maintenance and to reduce downtime risks.

## Slide 24: With fewer gravity pipe restrictions, the wet well depth could be reduced for safer operator access.
45’
The 60’ deep wet well would remain a challenge to maintain with limited operational flexibility

## Slide 25: Pumps will be replaced in the future to reach full buildout flows of 17 MGD and additional upgrades be limited.
The 60’ deep wet well would remain a challenge to maintain with limited operational flexibility

## Slide 26: The new lift station site reduced high risk items and provides the long-term solution for the District
Pros | Cons
Adequate pumping capacity Shallower wet well depth (45’) Easier access during inspection and maintenance Eliminates inverted siphon and related heavy solids deposition Lift station can be designed for easy expansion as contributing area continues to develop Limited use of bypass pumping Eliminates system surcharging Infrastructure in USACE property limited to pressure pipe and ARVs | Longest lead time for additional pumping capacity (2-3 years) Property acquisition needed for new lift station site Significant temporary construction easement needs
Cons
Pros
Adequate pumping capacity
Shallower wet well depth (45’)
Easier access during inspection and maintenance
Eliminates inverted siphon and related heavy solids deposition
Lift station can be designed for easy expansion as contributing area continues to develop
Significant temporary construction easement needs
Property acquisition needed for new lift station site
Longest lead time for additional pumping capacity (2-3 years)
Limited use of bypass pumping
Eliminates system surcharging
Infrastructure in USACE property limited to pressure pipe and ARVs

## Slide 27: Alternatives Summary
Alternative | Does it Meet the Critical Success Factors? |  |  |  |  | OPCC
 | Bypass flows from the WILS | Increases Pumping Capacity of the WILS | Mitigate Sediment Issues in 36-inch Siphon | Improves wet well accessibility for future maintenance | Minimize 100-year floodplain infrastructure and USACE Impact | 
New Lift Station, New Force Main, Decommission WILS | Yes | Yes | Yes | Yes | Yes | $16,526,250
Bypass Suction Pit, Rehab WILS, New Dry Weather Barrel Siphon | Yes | Yes | Yes | No | No | $7,792,500*
*Does not factor in future cost for a second future lift station to meet buildout flows

## Slide 28: Bidding update

## Slide 29: Bids were recently received for the Lift Station and lake crossing were in line with our original estimates.
WILS Bids | Total Bid
Bidder #1 | $11,953,375
Bidder #2 | $12,142,000
Bidder #3 | $12,430,000
Preliminary LS OPCC | $12,750,000
Lake Crossing Bids | Total Bid
Bidder #1 | $1,420,640
Preliminary HDD OPCC | $1,350,000